## Calc
Calculations for pressurized flow in circular cross section pipes
© D. Koutsoyiannis, 2008-2017
http://www.itia.ntua.gr/el/softinfo/32/
Method A: Based on the Darcy-Weisbach-Colebrook-White equations
The relevant equations are (see any of hydraulics books)
Variant 1: Use the Excel solver (note: you must have installed the Solver Add On in Excel)
Give the values of the three of the yellow cells and run the solver to find the fourth one
The solver should minimize the error in eqn (4) (cell in red font) by changing the cell whose value we are looking for
[6 empty] | ε (m) | D (m) | Q (m³/s) | J (-) | f (-) | Re (-) | V (m/s) |  | eqn (4) left | eqn (4) right | eqn (4) square error
[6 empty] | 0.001 | 0.3 | 0.1 | 0.0092791 | 0.027289 | 385830.2935 | 1.4147 |  | 6.0535 | 6.0535 | 2.5559e-28
Variant 2: Use the VBA functions contained in this file
See/Edit the VBA functions from the menu Developer - Visual Basic. You must have enabled macros to use them
|  | Simple function call |  |  |  |  | Detailed function call - all intermediate quantities are shown
|  | The single output is the required quantity |  |  |  |  | Note that the function works as an array function and needs a range of 2 x 7 cells
|  | ε (m) | D (m) | Q (m³/s) | J (-)
Problem 1: Find J for given Q, D |  | 0.001 | 0.3 | 0.1 | 0.0092791 |  | ε (m) | D (m) | Q (m³/s) | J (-) | f (-) | Re (-) | V (m/s)
[7 empty] | 0.001 | 0.3 | 0.1 | 0.0092791 | 0.027289 | 385830.491 | 1.4147
Problem 2: Find Q for given J, D |  | 0.001 | 0.3 | 0.1 | 0.0092791 |  | ε (m) | D (m) | Q (m³/s) | J (-) | f (-) | Re (-) | V (m/s)
[7 empty] | 0.001 | 0.3 | 0.1 | 0.0092791 | 0.027289 | 385830.5051 | 1.4147
Problem 3: Find D for given Q, J |  | 0.001 | 0.3 | 0.1 | 0.0092791 |  | ε (m) | D (m) | Q (m³/s) | J (-) | f (-) | Re (-) | V (m/s)
[7 empty] | 0.001 | 0.3 | 0.1 | 0.0092791 | 0.027289 | 385830.0287 | 1.4147
Variant 3: For romantic guys who like tradition
Use the Moody-Rouse graph which you can find in the shet "Moody" in this file
Problem 1: Find J for given Q, D
Problem 2: Find Q for given J, D
Problem 3: Find D for given Q, J
Method B: Based on the generalized Manning equation
Reference: D. Koutsoyiannis, A power-law approximation of the turbulent flow friction factor useful for the design and simulation of urban water networks, Urban Water Journal, 5 (2), 117–115, 2008.
The method can perform with typical spreadsheet calculations or in calculators based on the following equations:
V = (1/N) R (1+β)/2 J (1+γ)/2 (5)
Combined with (2), (5) results ineach of the following:
The parameters β, γ, Ν are determined in terms of a dimensionless roughness:
For typical ranges of diameters and velocities, they can be calculated as follows (for non-typical ranges see the above reference)
Note: β and γ are dimensionless while N is appropriate for the SI system (m, s)
Typical values of parameters
ε (m) | ε* | β | γ | N [SI]
0.001 | 20 | 0.31015 | 0.013333 | 0.01202
0.0001 | 2 | 0.30237 | 0.059259 | 0.0086432
Note: The error with respect to the DWCW method is also given for comparison
|  | ε (m) | ε* | β | γ | N [SI] | D (m) | Q (m³/s) | J (-) |  | % Difference from DWCW
Problem 1: Find J for given Q, D |  | 0.001 | 20 | 0.31015 | 0.013333 | 0.01202 | 0.3 | 0.1 | 0.009166 |  | -1.219%
Problem 2: Find Q for given J, D |  | 0.001 | 20 | 0.31015 | 0.013333 | 0.01202 | 0.3 | 0.10062 | 0.0092791 |  | 0.6234%
Problem 3: Find D for given Q, J |  | 0.001 | 20 | 0.31015 | 0.013333 | 0.01202 | 0.2993 | 0.1 | 0.0092791 |  | -0.2338%
Re=𝑉𝐷/𝜈 (1)
Q=(𝜋𝐷^2)/4 𝑉 (2)
𝐽=𝑓/𝐷 〖 𝑉〗^2/2𝑔 (3)
1/√𝑓=−2log_10((𝜀\/𝐷)/3.7+2.51/(Re√𝑓)) (4)
𝐽=((4^(3+𝛽) 𝑁^2 𝑄^2)/(π^2 𝐷^(5+𝛽) ))^(1/(1+𝛾)) (6)
𝑄=(π𝐷^((5+𝛽)/2) 〖 𝐽〗^((1+𝛾)/2) )/(2^(3+𝛽) 𝑁) (7)
𝐷=((4^(3+𝛽) 𝑁^2 𝑄^2)/(π^2 𝐽^(1+𝛾) ))^(1/(5+𝛽)) (8)
𝜀_∗≔𝜀/𝜀_0 , 𝜀_0≔(𝜈^2/𝑔)^(1\/3)=0.000 05 m (9)
𝛽=0.3+0.000 5 𝜀_∗+0.02/(1+6.8𝜀_∗ ) (10)
𝛾=0.096/(1+0.31𝜀_∗ ) (11)
𝛮=0.00687(1+1.6𝜀_∗ )^0.16 (12)